## Model and Assumptions
Production & Project |  | Comment
Project Lifetime | 20 | Yury
Project Year | 2023
LCFS discount USD per kg | 0.7 | Will probably disappear after 2030
Tax Rate | 21%
Production GH2 per day | 24286.7573 | (computed as a function of EL power+usage)
Economics
IRR | 12% | Val
Operating Days | 365 | Yury
Project Start Year | 2022 | Yury
Inflation Rate | 2.92% | (mean 2012-22) | https://www.usinflationcalculator.com/inflation/current-inflation-rates/#:~:text=The%20annual%20inflation%20rate%20for,ET.
Insurance Rate | 1.5% | (assume uniform)
Contingency | 10% | what is it? Adds additional 4.5 mil to Opex
Constants |  |  |  |  | 4799821.277 | 120806537.7
KWh per KG H2 | 33.6 |  |  |  | 1375772.095 | 39516875.87
Solar MWH produced per day from 1 MW | 6.58
Setup Type | Microgrid | Microgrid | Grid_PGE | Grid_CAISO
Costs
Grid Total Capex | 42643522.51 | 37843701.2293
Grid Total Opex (no Energy Cost) | 16823699.19 | 15447927.0933 |  |  |  |  | PGE B-20 Electricity Cost
Grid Total | 59467221.69 | 53291628.3227 | (user specified) | (user specified) |  |  | Mean MWh | 202
Grid Connection Power, MW (MVA) | 54.4529 | (by default use electrolyser power) | 50 | 50 |  |  | Demand Charge MW/MWh | 108.23
Grid Connection Type | CAISO | [5 empty] | Total | 310.23
[7 empty] | Transfer losses | 30% | (technical 2.5% + economics -- as taking at other timeframe)
Battery Total Capex | 148344396 | 27537858.3288
Battery Total Opex | 48267662.37 | 8750786.5
Battery Total | 196612058.4 | 36288644.8288 | (user specified) | (user specified)
Battery Capacity | 563.5517 |  | 100 | 50
Energy need to be stored/sent to grid (min, MWh) | 507.1965 | (bell curve integral approx)
Energy out of Battery with losses | 498.067 | [5 empty] | CAISO
[7 empty] | Mean MWh | 37.8
[7 empty] | Market loss | 46%
Solar Total Capex | 119676763.1
Solar Total Opex | 21696642.2
Solar Total | 141373405.3
Solar Power, MW | 200
Energy Produced by Solar, MWh | 1316 | (losses are included in the statistics)
Electrolyzer Total Capex | 101280088.2
Electrolyzer Total Opex | 20878665.06
Electrolyzer Total | 122158753.2
Electrolyzer Total with POSSIBLE ITC | 85511127.26 | (in a microgrid setup we can use ITC, but -3$ IRA is easier) | (user specified) | (user specified) | 122387819.4082 | 36876692.15
Electrolyser Power MW | 54.4529 | (demand vs heating value vs usage)
Electrolyser Energy Demand MWh per day | 1306.8704 |  | (user specified) | (user specified)
Electrolyzer Usage % | 100%
Leftover Energy | 5.1028e-05 | (should be 0, if negative EL use more energy than available)
(leftover = 0 iff microgrid)
Extra fee for grid usage (PGE) | 0
Extra fee for grid usage (CAISO) | 0
Labor Total | 46618172.98
Overall Expenses Beyond Electricity | 519611438.6
Electricity Expenses | 0
Overall Expenses | 519611438.6
GH2_Price | 7.01
IRA Discount | -3
Total | 4.01
Production | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Discounted Volume, KG | 74159821.22 | 8864666.423 | 7914880.735 | 7066857.799 | 6309694.463 | 5633655.771 | 5030049.795 | 4491115.889 | 4009924.901 | 3580290.09 | 3196687.58 | 2854185.339 | 2548379.767 | 2275339.078 | 2031552.748 | 1813886.382 | 1619541.413 | 1446019.119 | 1291088.499 | 1152757.588 | 1029247.847
Not counted yet:
degradation
DO NOT USE
Hydrogen Storage | 2022
Degradation over time | 0.25% | needs confirmation | https://gulfenergyinfo.com/h2tech/articles/2021/q3-2021/long-duration-h2-storage-in-solution-mined-salt-caverns-part-1#:~:text=H2%20in%20storage%20does,energy%20efficiency%20remains%20constant%20indefinitely.
Lifetime | 30 | (mid scenario) | https://www.nrel.gov/news/program/2020/answer-to-energy-storage-problem-could-be-hydrogen.html
Roundtrip Efficiency | 60% | (mid scenario) | https://www.nrel.gov/news/program/2020/answer-to-energy-storage-problem-could-be-hydrogen.html
Annual cost drop | 2% | (table 1, salt cavern based, extrapolated) | https://www.pnnl.gov/sites/default/files/media/file/Hydrogen_Methodology.pdf
DO NOT USE

## CFs
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Items | Units
General assumptions
Project Lifetime | years | 20
Project Year |  | 2023
Tax Rate | % | 21%
Days |  | 365
IRR | % | 12%
Operating Days | days | 365
Project Start Year |  | 2022
Inflation Rate | % | 2.92%
Insurance Rate | % | 1.5%
Contingency | % | 10%
PnL
Revenue
Volumes H2 produced | kg |  | 8864666.423 | 8686742.241 | 8512551.57 | 8341616.8 | 8175565.88 | 8012770.86 | 7853231.741 | 7696948.523 | 7542293.254 | 7390893.886 | 8864666.423 | 8686742.241 | 8512551.57 | 8341616.8 | 8175565.88 | 8012770.86 | 7853231.741 | 7696948.523 | 7542293.254 | 7390893.886
Price | $/kg |  | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01
Total Revenue | $ |  | 62141311.62 | 60894063.11 | 59672986.51 | 58474733.77 | 57310716.82 | 56169523.73 | 55051154.51 | 53955609.14 | 52871475.71 | 51810166.14 | 62141311.62 | 60894063.11 | 59672986.51 | 58474733.77 | 57310716.82 | 56169523.73 | 55051154.51 | 53955609.14 | 52871475.71 | 51810166.14
OPEX
Labor | $ |  | -4633588.014 | -4768888.784 | -4908140.337 | -5051458.035 | -5198960.609 | -5350770.259 | -5507012.751 | -5667817.523 | -5833317.795 | -6003650.674 | -6178957.274 | -6359382.826 | -6545076.805 | -6736193.048 | -6932889.885 | -7135330.269 | -7343681.913 | -7558117.425 | -7778814.454 | -8005955.836
Grid | $ |  | -1672182.439 | -1721010.166 | -1771263.663 | -1822984.562 | -1876215.711 | -1931001.21 | -1987386.445 | -2045418.129 | -2105144.339 | -2166614.553 | -2229879.698 | -2294992.186 | -2362005.957 | -2430976.531 | -2501961.046 | -2575018.309 | -2650208.843 | -2727594.941 | -2807240.714 | -2889212.142
Battery | $ |  | -5769656.9 | -5938130.881 | -6111524.303 | -6289980.813 | -6473648.253 | -6662678.782 | -6857229.002 | -7057460.089 | -7263537.923 | -7475633.231 | -7693921.721 | -7918584.235 | -8149806.895 | -8387781.256 | -8632704.469 | -8884779.44 | -9144214.999 | -9411226.077 | -9686033.879 | -9968866.068
Solar | $ |  | -2593500 | -2669230.2 | -2747171.722 | -2827389.136 | -2909948.899 | -2994919.407 | -3082371.053 | -3172376.288 | -3265009.676 | -3360347.958 | -3458470.119 | -3559457.446 | -3663393.604 | -3770364.697 | -3880459.346 | -3993768.759 | -4110386.807 | -4230410.101 | -4353938.076 | -4481073.068
Electrolyzer | $ |  | -2492189.583 | -2564961.519 | -2639858.396 | -2716942.261 | -2796276.975 | -2877928.262 | -2961963.768 | -3048453.11 | -3137467.94 | -3229082.004 | -3323371.199 | -3420413.638 | -3520289.716 | -3623082.176 | -3728876.175 | -3837759.36 | -3949821.933 | -4065156.733 | -4183859.31 | -4306028.002
Electricity | $
Total Opex | $ |  | -17161116.94 | -17662221.55 | -18177958.42 | -18708754.81 | -19255050.45 | -19817297.92 | -20395963.02 | -20991525.14 | -21604477.67 | -22235328.42 | -22884600.01 | -23552830.33 | -24240572.98 | -24948397.71 | -25676890.92 | -26426656.14 | -27198314.5 | -27992505.28 | -28809886.43 | -29651135.12
EBITDA | $ |  | 44980194.69 | 43231841.56 | 41495028.09 | 39765978.96 | 38055666.37 | 36352225.81 | 34655191.49 | 32964084 | 31266998.04 | 29574837.72 | 39256711.61 | 37341232.78 | 35432413.53 | 33526336.06 | 31633825.9 | 29742867.6 | 27852840.01 | 25963103.86 | 24061589.28 | 22159031.02
EBITDA margin | % |  | 72.38% | 71% | 69.54% | 68.01% | 66.4% | 64.72% | 62.95% | 61.09% | 59.14% | 57.08% | 63.17% | 61.32% | 59.38% | 57.33% | 55.2% | 52.95% | 50.59% | 48.12% | 45.51% | 42.77%
Depriciation (IRS) | $ |  | -72967109.76 | -116747375.6 | -70048425.37 | -41956088.11 | -41956088.11 | -21160461.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tax Expense | $ |  | 0 | 0 | 0 | 0 | 0 | -3190270.436 | -7277590.212 | -6922457.641 | -6566069.588 | -6210715.921 | -8243909.439 | -7841658.884 | -7440806.842 | -7040530.572 | -6643103.438 | -6246002.195 | -5849096.402 | -5452251.812 | -5052933.748 | -4653396.515
After-Tax Net Equity Cash Flow | $ |  | -27986915.08 | -73515534.06 | -28553397.29 | -2190109.153 | -3900421.742 | 12001493.54 | 27377601.28 | 26041626.36 | 24700928.45 | 23364121.8 | 31012802.17 | 29499573.9 | 27991606.69 | 26485805.49 | 24990722.46 | 23496865.4 | 22003743.61 | 20510852.05 | 19008655.53 | 17505634.51
Tax shield | $ |  | 15323093.05 | 24516948.88 | 14710169.33 | 8810778.504 | 8810778.504 | 4443696.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
After-Tax Net Equity Cash Flow (adj. for non-cash expense) | $ |  | 44980194.69 | 43231841.56 | 41495028.09 | 39765978.96 | 38055666.37 | 33161955.38 | 27377601.28 | 26041626.36 | 24700928.45 | 23364121.8 | 31012802.17 | 29499573.9 | 27991606.69 | 26485805.49 | 24990722.46 | 23496865.4 | 22003743.61 | 20510852.05 | 19008655.53 | 17505634.51
Net Present Value | $ | 41049822.11 | -11306983.95 | -39061372.11 | -9853336.226 | 4207555.064 | 2786268.298 | 8331645.316 | 12384236.45 | 10517776.12 | 8907402.425 | 7522621.915 | 8915439.546 | 7571805.872 | 6414953.794 | 5419520.556 | 4565711.56 | 3832847.732 | 3204720.736 | 2667222.794 | 2207033.727 | 1814752.5
Net Present Value (adj. for non-cash expense) | $ | 661296670 | 60303287.74 | 67748790.44 | 56205197.42 | 48576757.46 | 46866444.88 | 37605652.36 | 27377601.28 | 26041626.36 | 24700928.45 | 23364121.8 | 31012802.17 | 29499573.9 | 27991606.69 | 26485805.49 | 24990722.46 | 23496865.4 | 22003743.61 | 20510852.05 | 19008655.53 | 17505634.51
Grid Capex | $ | -42643522.51
Electrolyzer Capex | $ | -101280088.2
Battery Capex | $ | -195911720
Battery Subsidy | % | 30%
Battery Sub. Capex | $ | -137138204
Solar Capex | $ | -119676763.1
Solar Subsidy | % | 30%
Solar Sub. Capex | $ | -83773734.14
Total Capex incl. subsidy | $ | -364835548.8
Total Capex w/o subsidy | $ | -459512093.7
LCFS discount USD per kg |  |  | 1: 0.7

## D&A
PV (Solar) |  | Power Grid |  |  | Aircraft
AC-DC inverter
`
DC-DC coverter |  | AC-DC coverter |  |  | Fuel Cell
| Battery |  | Electrolyser |  | H2 Storage
Elements
DC-DC converter -- adjust voltage and stabilize it
AC-DC inverter -- takes DC, outputs AC
PV + DC-DC converter -- the same block
Element | Cost - USD per MW/MWh | Depteciation time | Lifetime | Time to Charge | Time to Discharge | Links
Solar/PV | 900000 | 6 | 15 | n/a | n/a | https://www.solarreviews.com/blog/what-is-a-solar-farm-do-i-need-one
DC-DC converter | 0 | 6 | 15 | n/a
AC-DC inverter | 300000 | 6 | 10 | n/a
Battery | 300000 | 6 | 10 | 8 | 4
Electrolyser | 380000 | 6 | 10
H2 Turbine | 1300000 | 6 | 15
H2 storage | 1500000 | 6 | 20
Performance Degradation/year:
Solar/PV | 0.5%
Battery | 2.5%
Depreciation | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6
PV schedule | 20% | 32% | 19.2% | 11.5% | 11.5% | 5.8%
Electrolyser | 20% | 32% | 19.2% | 11.5% | 11.5% | 5.8%
AC-DC Converter | 20% | 32% | 19.2% | 11.5% | 11.5% | 5.8%
H2 turbine | 20% | 32% | 19.2% | 11.5% | 11.5% | 5.8%
H2 storage | 20% | 32% | 19.2% | 11.5% | 11.5% | 5.8%
Battery | 20% | 32% | 19.2% | 11.5% | 11.5% | 5.8%

## GRID Capex-Opex
Grid Connection/System Size, MW | 54.4529 |  | (equals to electrolyser power size)
Grid Connection Type | CAISO | PGE B20 | PGE WDAT | CAISO
Transmission ITC | 30% | Range from 6% Base to 30% Bonus | https://www.foley.com/en/insights/publications/2021/10/new-tax-credit-electric-transmission-property
Lifetime | 50 |  | https://www.infrastructurereportcard.org/wp-content/uploads/2017/01/Energy-Final.pdf
Grid Overhead | 10%
Grid O&M | 1.5%
Grid Insurance | 1.5%
CAISO Grid (single 45 MVA connection) | CapEx | Annual Opex | Comment | Question | URL
substation_construction | 18600000 | 0 |  |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
substation_regulatory | 6000000 | 0 |  |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
substation_land | 2400000 | 0 | 5 Arce Parcel |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
transformer | 11800000 | 0 | <= 45 MVA |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
circuit_switcher | 2200000 | 0 |  |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
breakers | 1400000 | 0 |  |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
indoor_outlets | 1100 | 0 |  |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_New | 160 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_Reconductor | 160 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_capacitor | 33000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_switch | 30000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_scada_switch | 45000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_regulator | 150000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_recloser | 80000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_fuse | 10000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
OH_scada | 15000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
reclocate_capacitor | 18000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
UG_new_w_trench | 320 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
transformer_replace | 34000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
autotransformer | 850000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
UG_switch | 80000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
UG_scada | 130000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
UG_interrupter | 120000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
PM_capacitor | 65000 | 0 | Non-Bay |  | https://www.pge.com/pge_global/common/pdfs/about-pge/company-information/regulation/contracts-and-tariffs/WDT-Unit-Costs.pdf
contingency | 4406174 | 0 | 10% for all grid capex items
om_operations_maintenence | 0 | 660926 | 1.5% for each
insurance | 0 | 660926 | 1.5% for each
security_deposit | 224083.3087 | 0 | 250000 k security deposit for 20+MW system, discounted in time (3% IRS rate, 20 years), $100k smaller |  | http://www.caiso.com/Documents/LSACommentsonSmallandLargeGeneratorInterconnectionProceduresDraftFinalProposalandMeeting.pdf
ISF | 1089058.676 |  | IFS = Interconnection Financial Security, mean of Page 4 |  | http://www.caiso.com/Documents/LSACommentsonSmallandLargeGeneratorInterconnectionProceduresDraftFinalProposalandMeeting.pdf
metering | 0 | 60042.5 | 164.5 per day
ITC discount | -14540374.2 | 0
| 35240681.78 | 1381894.5 | (per single connection)
PG&E Grid (single 20 MVA max connection) | CapEx | Annual Opex | Comment | Question | URL
distritution_upgrade (B-20 only) | 1089058.676 | 0 |  |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
transmission_upgrade (B-20 only) | 7500000 | 0 |  |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
ITC discount (B-20 only) | -2250000 | 0
metering (B-20 only) | 0 | 21280 | 58.30 per day if secondary voltage grid |  | https://www.pge.com/tariffs/assets/pdf/tariffbook/ELEC_SCHEDS_B-20.pdf
metering (WDAT only) | 0 | 60042.5 | 164.5 per day |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
deposit (WDAT only) | 13444998.52 | 0 |  |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
cost_ownership (WDAT only) | 0 | 311906.4049 |  |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
infrastructure_rent_cost (WDAT only) | 0 | 2537956 | 0.48% per month |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
ISF (WDAT only) | 1089058.676 | 0 |  |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
security_deposit (WDAT only) | 235672.3518 | 0 |  |  | https://www.pge.com/includes/docs/pdfs/shared/customerservice/nonpgeutility/electrictransmission/tariffs/PGE_Wholesale_Distribution_Tariff.pdf
| 14769729.55 | 2909904.905 | (per single connection)
Grid Connection & Service Cost | 42643522.51 | 1672182.439 | (assuming > 45 MW lead to a linear increase for CAISO & PGE) |  |  |  | Добавить третий сценарий
Spanned Across Project Duration | Project Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Capex | 42643522.51 | 42643522.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex | 16823699.19 | 1672182.439 | 1536616.22 | 1412040.55 | 1297564.41 | 1192369.01 | 1095701.95 | 1006871.83 | 925243.29 | 850232.49 | 781302.93 | 717961.59 | 659755.42 | 606268.11 | 557117.09 | 511950.81 | 470446.23 | 432306.48 | 397258.78 | 365052.44 | 335457.12
Grid Total (with ITC Bonus) | 59467221.69

## Labor Opex
FTE, Electolyzer | 4 | to cover 24/7 | (per 20 MW, Arnab)
FTE, Battery + Solar | 4 | to cover 24/7 | (per 40 MW Solar system)
Unit FTE | 150000
Total Opex 1st year | 4633588.014
Spanned Across Project Duration | Project Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Opex | 46618172.98 | 4633588.014 | 4257936.41 | 3912739.42 | 3595528.05 | 3304033.45 | 3036170.74 | 2790024.04 | 2563832.81 | 2355979.22 | 2164976.62 | 1989458.87 | 1828170.6 | 1679958.2 | 1543761.59 | 1418606.63 | 1303598.16 | 1197913.59 | 1100797.02 | 1011553.83 | 929545.72
Labor Total | 46618172.98

## Battery Capex-Opex
Project Start Year | 2023
Battery
2nd life MWH price/1st life MWH price | 0.53 |  | https://www.sciencedirect.com/science/article/abs/pii/S0306261921007212
Degradation Rate per Year | 2% | YM | https://ieeexplore.ieee.org/document/9223659
Battery loss | 1.8% | (Sarnoff-wood: operating under 0.3C)
State of Charge Max: | 5% | (Sarnoff-wood: battery health)
State of Charge Min: | 95% | (Sarnoff-wood: battery health)
Depth of charge | 90%
Correction coeff. for upsized battery | 0.9 | (economic literature) | not used currently, yet there is upsize potential
Annual cost drop rate | 3% | Figure ES-2, GeoMean from 2020-35 | https://www.nrel.gov/docs/fy21osti/79236.pdf
Lifetime | 10 | (at 0.8 capacity) | https://blog.modo.energy/battery-degradation-explained
Investment Tax Credit | 30% | (specific components only) | https://www.troutman.com/insights/new-ira-tax-incentives-for-us-manufacturing-in-renewable-energy-sector.html
Battery capacity, MWh | 563.55
Battery Replacement year | 10
Battery structure | Capex per MWH | Opex per MWH-year | (based on 120 MWh system estimate)
energy_per_2C | 215000 | 0 | $152 per 163 Ah at 3.2 V, 2C (Sarnoff-Wood). Wh = Ah*V |  |  |  | https://www.electriccarpartscompany.com/163ah-calb-batteries-l173f163b
inverter_per_MW | 37000 | 7400 | should take C = 2/3, 0.15W for 3 phase bi directional; table A-1; Inv failure issue - SE |  |  |  | https://atb.nrel.gov/electricity/2021/commercial_battery_storage
structural_BOS | 5000 | 500 | BOS = Balance of system, table 17 |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
elecrical_BOS | 50000 | 5000 | BOS = Balance of system, table 17 |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
permitting | 30000 | 0 | table 17, 0.03 per W |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
labor_construction | 14400 | 0 | 2 weeks of 2.0 FTE Electrician and 2 weeks of 4.0 FTE labor with 0.4 overhead |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
epc_overhead_matherials | 26616.9 | 0 | according to NREL |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
developer_overhead | 12900 | 0 | 3% according to NREL |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
developer_profit | 21500 | 0 | 5% according to NREL |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
om_operations_maintenance | 0 | 6186.2535 | 1.5% according to NREL |  |  | (table 17) | https://www.nrel.gov/docs/fy21osti/77324.pdf
contingency | 41241.69 | 0 | 10% is assumed
Total per MW (no tax shield) | 453658.59 | 19086.2535
Economy of scale (per MW) | 0.79 | 0.79 | (piece-wise linear at lower levels, exp at higher levels, limited by tha stack&inverter cost + 10% overhead) | https://atb.nrel.gov/electricity/2022/utility-scale_battery_storage +H3 proposal
Correction to the project start FY | 0.97 | 0.97
Cost w/o ITC, USD -- FY 2022 | 195911720 | 8242367
Cost with ITC, USD -- FY 2022 | 137138204 | 5769656.9 | (no labor/insurance -- ITC applied in full for the system upgrade)
Assumptions:
Non labor opex is deflated with the cost drop rate
Labor opex is inflated with the inflation rate
Capex Decreases with the cost drop rate
Labor is computed separately
Battery: 1.5 -- 2 cycles per day |  | 80% degradation at the EOL | https://blog.modo.energy/battery-degradation-explained
Battery: Uniform Degradation MWH over time |  |  | https://www.iso-ne.com/static-assets/documents/2020/12/a9_modeling_of_battery_storage_in_economic_studies.pdf
Battery: No degradation MW over time |  |  | https://www.iso-ne.com/static-assets/documents/2020/12/a9_modeling_of_battery_storage_in_economic_studies.pdf
Spanned Across Project Duration | Project Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Capex | 148344396 | 137138204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17257244.14 | 32560837.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4097401.849
Opex | 48267662.37 | 5769656.9 | 5151479.38 | 4599535.16 | 4106727.82 | 3666721.27 | 3273858.28 | 2923087.75 | 2609899.78 | 2330267.66 | 2080596.13 | 0 | 1857675.12 | 1658638.5 | 1480927.23 | 1322256.46 | 1180586.13 | 1054094.76 | 941156.04 | 840317.89 | 750283.83 | 669896.28 | 0
Capacity nominal MAX, MWh | 515.442 | 563.55 | 552.28 | 541.23 | 530.41 | 519.8 | 509.4 | 499.21 | 489.23 | 479.45 | 469.86 |  | 563.55 | 552.28 | 541.23 | 530.41 | 519.8 | 509.4 | 499.21 | 489.23 | 479.45 | 469.86
Battery Total | 196612058.4

## Solar Capex-Opex
Solar Size, MW | 200
Project Year | 2023
Investment Tax Credit (ITC) | 30% | Yury: IRA based | https://geniesolarenergy.com/2022-ira-commercial-solar-implications/
Bonus ITC | 10% | if domestic labor met | https://geniesolarenergy.com/2022-ira-commercial-solar-implications/
Lifetime | 30 | industry survey | https://emp.lbl.gov/publications/benchmarking-utility-scale-pv
Mean Degradation Rate per Year | 0.5% | Yury: averaged | https://www.nrel.gov/state-local-tribal/blog/posts/stat-faqs-part2-lifetime-of-pv-panels.html
Inverter + System Loss | 3% | Check | https://www.solarempower.com/blog/10-solar-pv-system-losses-their-impact-on-solar-panel-output/
Cost Drop Rate | 2.5% | Mean scenario DOE averaged with NREL | https://www.energy.gov/eere/solar/articles/2030-solar-cost-targets | https://atb.nrel.gov/electricity/2022/utility-scale_pv#capital_expenditures_(capex)
Solar secondary market discount | 0.64 |  | https://www.technologyreview.com/2021/08/19/1032215/solar-panels-recycling/#:~:text=A%20second%20life&text=A%20panel%20might%20cost%20around,recycling%20startup%20called%20TG%20Companies.
Solar losses | 3% |  | https://www.solarempower.com/blog/how-much-money-1-acre-solar-panels-make-income/
Assumptions
monocrystalline solar
all systems are utility scale -- 10 MW and up
1 sq meter = 200 W power, 1 KW = 4.8 sq mt | 4.8
Powe-to-energy ratio (C) | 0.6
(20+ MW system estimate) | Fixed Capex | Variable CaPex per MW | Capex for the System
module | 0 | 330000 | 66000000 | page 24 for commeercial | https://www.nrel.gov/docs/fy22osti/83586.pdf
inverter | 0 | 27000 | 5400000 | W_ac for C = 0.6 | https://www.nrel.gov/docs/fy22osti/83586.pdf
structural_BOS | 0 | 144960 | 28992000 |  | https://www.nrel.gov/docs/fy22osti/83586.pdf
electrical_BOS | 69000 | 75840 | 15237000 |  | https://www.nrel.gov/docs/fy22osti/83586.pdf
intallation_labor | 0 | 52416 | 10483200 |  | https://www.nrel.gov/docs/fy22osti/83586.pdf | [6 empty] | 20
installation rental equipement | 0 | 59040 | 11808000
Construction Overhead | 106000 | 51531.36 | 10412272 |  | https://www.nrel.gov/docs/fy22osti/83586.pdf
permitting (PII) | 209466 | 12000 | 2609466 | (interver based) | https://www.nrel.gov/docs/fy22osti/83586.pdf
Developer Overhead | 550000 | 11291.8104 | 2808362.08 |  | https://www.nrel.gov/docs/fy22osti/83586.pdf
contingency | 93446.6 | 76407.917 | 15375030.01 |  | https://www.nrel.gov/docs/fy22osti/83586.pdf
Developer Profit | 200000 | 41183.8673 | 8436773.457
Total FY 22 | 1227912.6 | 881670.9547 | 177562103.5 |  | https://www.solarempower.com/blog/how-much-money-1-acre-solar-panels-make-income/
Total for the project start year |  |  | 173123051
Total with ITC |  |  | 121186135.7
Opex | Opex Fixed | Opex per MW | Opex for the System
Operations and Maintenance | 0 | 6500 | 1300000 |  | https://eta-publications.lbl.gov/sites/default/files/solar_life_and_opex_report.pdf
Other opex (insurance, upgrade, etc) | 0 | 12500 | 2500000 |  | https://www.nrel.gov/docs/fy20osti/74840.pdf
Total FY 22 |  |  | 3800000
Total for the project start year |  |  | 3705000
Total with ITC |  |  | 2593500 |  | Applicable as equipement only
Spanned Across Project Duration | Project Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Resale
Capex | 119676763.1 | 121186135.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1509372.611
Opex | 21696642.2 | 2593500 | 2315625 | 2067522.32 | 1846002.07 | 1648216.13 | 1471621.54 | 1313947.8 | 1173167.68 | 1047471.14 | 935242.09 | 835037.58 | 745569.27 | 665686.85 | 594363.26 | 530681.48 | 473822.75 | 423056.03 | 377728.6 | 337257.68 | 301122.93
Power nominal MAX, MWh | 200 | 199 | 198.01 | 197.02 | 196.03 | 195.05 | 194.07 | 193.1 | 192.13 | 191.17 | 190.21 | 189.26 | 188.31 | 187.37 | 186.43 | 185.5 | 184.57 | 183.65 | 182.73 | 181.82 | 180.91
Solar cost total | 141373405.3

## Electrolyzer Capex-Opex
Project Start Year | 2023
Electrolyzer power, MW | 54.4529
Hours lifetime | 70000 | (averaged across PEM/AEM) | https://www.sciencedirect.com/science/article/pii/S0360319917339435
Investment Tax Credit | 30% |  | https://www.bakerbotts.com/thought-leadership/publications/2022/august/clean-hydrogen-and-fuel-cell-incentives-in-the-inflation-reduction-act-of-2022
Price drop per Year | 10% | (mean over incoherent) | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf |  | https://www.pnnl.gov/sites/default/files/media/file/Hydrogen_Methodology.pdf
Electrolyser Efficiency Increase Annual | 1.5% | 90% HT + 80% LT DOE Goal -- Geometric Span | https://www.mdpi.com/1996-1073/15/4/1415
Electrolyser Efficiency | 61.5% | Table 3 + industry poll | https://www.mdpi.com/1996-1073/15/4/1415
Heating value | 53.81 | Table 3 + industry poll | https://www.mdpi.com/1996-1073/15/4/1415
Compression Losses | 14% | 700 bar | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf
(20 MW study) | CaPex per MW | Opex per MW (Equipement) | Opex per KG (Utilities) | Comment | Source
alkaline_electrolyser_per_MW | 445000 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
balance_of_plan_per_MW | 334500 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
export_panel_per_MW | 30000 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
control_sys_RGP_per_MW | 14500 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
4x_hofer_comp_per_MW | 164000 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
4x_capacity_control_bypass_value | 3000 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
4x_closed_loop_cooling | 7500 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
shipping_electrolyser | 32500 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
shipping_other | 5000 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
capex_contingency | 102750 | 0 | 0 | 30% for TGP 10% for the rest | Arnab Electrolyser Databook
utiliies | 44500 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
fire_protection | 5500 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
civil_work | 6750 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
mechanical_scope | 135000 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
site_scoping | 500 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
electrical | 90000 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
engineering_permits_indirect | 47900 | 0 | 0 | Alkaline 20 MW/per MW | Arnab Electrolyser Databook
construction_contingency | 99045 | 0 | 0 | Quote from EPC firm, 30% | Arnab Electrolyser Databook
decomissining | 73631.7991 | 0 | 0 | ? 10% (Arnab). Questionable -- not inflated | Arnab Electrolyser Databook
om_operations_maintenence | 0 | 34947.5 | 0 | ? 3.5% (Arnab). Questionable -- not inflated | Arnab Electrolyser Databook
om_compressor | 0 | 10500 | 0 | Not inflated? | Arnab Electrolyser Databook
water | 0 | 0 | 0.70796 | 16 kg H20 = 1 kg H2, $3.85 per 3000 kg (100 ft3) + 3897 metering fee | https://www.energy.gov/sites/prod/files/2017/10/f38/water_wastewater_escalation_rate_study.pdf
water_ca_fee | 0 | 0 | 0.010124 | 1.43% public utility comission fee | Arnab Electrolyser Databook
decomission_active_walls | 22500 | 0 | 0 | Drop off? Noone signed off. Alkaline 20 MW/per MW | Arnab Electrolyser Databook
| 1664076.799 | 45447.5 | 0.71808
https://www.nrel.gov/hydrogen/assets/docs/current-central-pem-electrolysis-v3-2018.xlsm
Economy of scale factor | 0.97 | (0.9 = 10x scaling factor), geometric mean | https://www.cell.com/cell-reports-physical-science/pdfExtended/S2666-3864(20)30224-1
Economy of time | 0.9
Scale & Time Adjusted Capex | 1452739.046
(efficiency parity)
Spanned Across Project Duration | Project Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Capex | 101280088.2 | 79105903.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22174185.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex (MW nominal) | 20703203.83 | 2474749.709 | 2209597.95 | 1972855.31 | 1761477.96 | 1572748.18 | 1404239.45 | 1253785.22 | 1119451.09 | 999509.9 | 892419.55 | 796803.17 | 711431.4 | 635206.61 | 567148.76 | 506382.82 | 452127.52 | 403685.29 | 360433.29 | 321815.44 | 287335.21
Opex (KG produced) | 175461.2308 | 17439.8738 | 16025.9983 | 14726.7478 | 13532.8293 | 12435.7035 | 11427.5232 | 10501.0776 | 9649.7402 | 8867.422 | 8148.5274 | 7487.9147 | 6880.8587 | 6323.0177 | 5810.4016 | 5339.3441 | 4906.4758 | 4508.7008 | 4143.174 | 3807.281 | 3498.6192
Opex (total) | 20878665.06
Power (max) nominal MAX, MWh | 49.8033 | 54.4529 | 53.36 | 52.29 | 51.24 | 50.22 | 49.22 | 48.24 | 47.28 | 46.33 | 45.4 | 54.4529 | 53.36 | 52.29 | 51.24 | 50.22 | 49.22 | 48.24 | 47.28 | 46.33 | 45.4
Electolyser_Total | 122158753.2
Electolyser_Total_With_ITC | 85511127.26

## Comments
1. | Degradation is used only in production. OPEX sticks to installed nominal capacity --> margin decline over time
2. | Costs grow at CPI, discounted by IRR
TODO:
1. | Electricity expense calculate for each year on CFs tab (yearly expense, without discount)
2. | Cross-check total opex on CFs tab vs. total opex by streams